## Slide 1
1
MODELLING AND SIMULATION OF A HEATING SYSTEM OF A SINGLE-FAMILY HOUSE
CASE STUDY
Presented By:
Eduardo Guandulain Juárez
Muhammad Munam Uddin Farooqui
Rohit Arunachalam Gopinath
Yuganshu Wadhwa
Nnamdi Ogbonnaya Odii

## Slide 2
AGENDA
Introduction
The Refrigeration Cycle
Heat Pump and Building Plant: UniSim
PRBS Tests
System Identification
Simulink Model and PI Control
OPC DA: Connecting Plant and Controller
Simulation Results
Testing Different Gains with the Plant
Testing Different Lags with the Plant
Eventual PI Controller
Conclusions and Future Possibilities

## Slide 3
SOLUTION APPROACH
The objective of this case study is to model and control a heating system for a single-family house.
Development of a plant model as well as an advanced PI controller in Simulink using system identification.
Using the developed controller to control the heat pump plant in UniSim via OPC DA communication channel.
WHY HEAT PUMP?
Economic reasons / cost saving.
Lower carbon footprint.
Energy efficiency - as heat pump transfers heat rather than generate it and produces 3-4 units of electricity for every unit of electricity consumed.
PROBLEM STATEMENT

## Slide 4
THE REFRIGERATION CYCLE
1
2
3
4
https://www.torr-engineering.com/the-refrigeration-cycle/

## Slide 5
HEAT PUMP MODEL: UNISIM
1
2
3
4

## Slide 6
PSEUDO-RANDOM BINARY SEQUENCE
(PRBS)

## Slide 7
PSEUDO-RANDOM BINARY SEQUENCE (PRBS) TESTS
Why?
      Dynamic Behavior of the system
      Accurate Model
Outcome
Linear Transfer Function
Notes: PRBS Test is widely used method
in system identification.
In our case we utilized the PRBS Tests to achieve 2 Main objectives.
1. Understand the Dynamic Behavior of the Heat Pump at different Stationary Points
2. And to develop an accurate model of the system in Simulink.
After doing the PRBS Tests we were able to establish the linear transfer function

## Slide 8
PSEUDO-RANDOM BINARY SEQUENCE (PRBS)TESTS
T_Out (°C) | PV_Stationary (°C) | OP_Stationary (%)
-12 | 33.902 | 97.0368
-11 | 33.7435 | 76.6963
-10 | 33.59 | 62.64
-9 | 33.4265 | 52.4591
-8 | 33.26 | 44.62
-5 | 32.62 | 30.45
-2 | 32.5 | 22.05
-1 | 32.17 | 19.96
0 | 31.92 | 18
1 | 31.84 | 16
2 | 31.69 | 14.45
Min OP: 10%
Min OP: 100%
Notes: We performed PRBS tests across a range of outside temperatures starting from +2 to -12 degrees Celsius.
It helped us understand how to system behaves under various conditions covering both min and max operating points.

## Slide 9
PSEUDO-RANDOM BINARY SEQUENCE (PRBS)TESTS
Notes: We began by running the unisim plant model with its inbuilt controller until it reached a stables operating point.
Once stable we conducted tests by applying a step change of +4 and -4 in the OP, during which we recorded the corresponding PV values
These steps allowed us to establish the steady state relationship between OP & PV
At certain temperatures we observed some spikes which was a characteristic behavior of the model.

## Slide 10
PSEUDO-RANDOM BINARY SEQUENCE (PRBS)TESTS
Notes: Each of the PRBS tests were run for 24 hours. We then converted the recorded values into delta values which represent the change in OP and PV
These delta values were then used further during the system identification process.

## Slide 11
SYSTEM IDENTIFICATION
Timestamp
PV
From Unisim
From Simulink

## Slide 12
T_Out (°C) | PV_Stationary (°C) | OP_Stationary (%) | V | T1 (s) | Ti (s) | Ti (days)
-12 | 33.902 | 97.0368 | 0.01 | 9784.27 | 4025452 | 46.59
-11 | 33.7435 | 76.6963 | 0.01 | 242.77 | 1838599 | 21.28
-10 | 33.59 | 62.64 | 0.0165 | 180 | 1650000 | 19.09722
-9 | 33.4265 | 52.4591 | 0.019 | 250.49 | 1073817 | 12.42844
-8 | 33.26 | 44.62 | 0.025 | 250 | 949536 | 10.99
-5 | 32.62 | 30.45 | 0.06 | 300 | 550000 | 6.365741
-2 | 32.5 | 22.05 | 0.08 | 300 | 400000 | 4.62963
-1 | 32.17 | 19.96 | 0.08 | 300 | 220000 | 2.546296
0 | 31.92 | 18 | 0.13 | 300 | 300000 | 3.472222
1 | 31.84 | 16 | 0.11 | 300 | 280000 | 3.240741
2 | 31.69 | 14.45 | 0.1 | 300 | 250000 | 2.893519
SYSTEM IDENTIFICATION – PARAMETER ESTIMATION

## Slide 13
Chart: Integrator Time Constant- Ti
| 97.036799999999999 | 76.696299999999994 | 62.64 | 52.459099999999999 | 44.62 | 30.45 | 22.05 | 19.96 | 18 | 16 | 14.45
97.0368 76.6963 62.64 52.4591 44.62 30.45 22.05 19.96 18 16 14.45 | 4025452 | 1838599 | 1650000 | 1073817 | 949536 | 550000 | 400000 | 220000 | 300000 | 280000 | 250000
SYSTEM IDENTIFICATION – PARAMETER ESTIMATION

## Slide 14
Chart: Gain - V
| 97.036799999999999 | 76.696299999999994 | 62.64 | 52.459099999999999 | 44.62 | 30.45 | 22.05 | 19.96 | 18 | 16 | 14.45
 | 0.01 | 0.01 | 0.0165 | 0.019 | 0.025 | 0.06 | 0.08 | 0.08 | 0.13 | 0.11 | 0.1
SYSTEM IDENTIFICATION – PARAMETER ESTIMATION

## Slide 15
SYSTEM IDENTIFICATION – NON LINEAR STATIONARY CURVE
Chart: Non Linear Stationary Curve
| 97.036799999999999 | 76.696299999999994 | 62.64 | 52.459099999999999 | 44.62 | 30.45 | 22.05 | 19.96 | 18 | 16 | 14.45
 | 33.902 | 33.7435 | 33.59 | 33.4265 | 33.26 | 32.62 | 32.5 | 32.17 | 31.92 | 31.84 | 31.69

## Slide 16
SYSTEM IDENTIFICATION – EFFECT OF DISTURBANCE Tout
Chart: Tout vs OP
| -12 | -11 | -10 | -9 | -8 | -5 | -2 | -1 | 0 | 1 | 2
 | 97.0368 | 76.6963 | 62.64 | 52.4591 | 44.62 | 30.45 | 22.05 | 19.96 | 18 | 16 | 14.45

## Slide 17
SYSTEM IDENTIFICATION – SETPOINT TRACKING
Chart: PV VS OP
| 33.902000000000001 | 33.743499999999997 | 33.590000000000003 | 33.426499999999997 | 33.26 | 32.619999999999997 | 32.5 | 32.17 | 31.92 | 31.84 | 31.69
 | 97.0368 | 76.6963 | 62.64 | 52.4591 | 44.62 | 30.45 | 22.05 | 19.96 | 18 | 16 | 14.45
OP

## Slide 18
PLANT MODEL

## Slide 19
PV
OP
Nonlinear Stationary Model
Linear Delta Model
Nonlinear Stationary Model
Linear Delta Model
PLANT MODEL

## Slide 20
Nonlinear Stationary Model
Linear Delta Model

## Slide 21
Nonlinear Stationary Model
Linear Delta Model
4

## Slide 22
4

## Slide 25
Open Platform Communications Data Access (OPC DA)

## Slide 26
OPC DA
Industrial Standard – For data communication.
Exchange of data between Hardware & Software.
Architecture
OPC Server – Acts as a data source for all clients – Matrikon Server
OPC Client – Requests data from the server – Matrikon Explorer
            Read Values
            Write Values
Simulink
UniSim
PV
PV
PV
OP

## Slide 27
INTEGRATING OPC DA WITH SIMULINK AND UNISIM
Simulink
UniSim
Read - PV
Write - PV
Read - OP
Write - OP
Client
Server
Matrikon Explorer
Matrikon Server

## Slide 28
SIMULINK WITH OPC DA COMMUNICATION BLOCKS
Notes: We are now ready to implement the developed PI Controller on the UniSim Plant model

## Slide 29
SIMULATED BEHAVIOUR

## Slide 30
CONTROL ACTION

## Slide 31
BEHAVIOUR AGAINST SETPOINT CHANGE

## Slide 32
BEHAVIOUR AGAINST VARYING DISTURBANCE

## Slide 33
TESTING WITH THE REAL PLANT

## Slide 34
SIMULATION RESULTS – GAIN TUNING

## Slide 35
SIMULATION RESULTS – GAIN TUNING

## Slide 36
SIMULATION RESULTS – GAIN TUNING

## Slide 37
SIMULATION RESULTS – DIFFERENT LAG VALUES

## Slide 38
SIMULATION RESULTS – DIFFERENT LAG VALUES

## Slide 39: DAY/NIGHT SIMULATION

## Slide 40
SIMULATION RESULTS – BEST PARAMETERS
Simulink
UniSim

## Slide 41
THANK YOU